Data Center Power & Electrical Basics

How power moves from the grid to the chip

Grid / on-site generation → voltage transformation → switching & protection → backup / ride-through → low-voltage distribution → rack power conversion → chip-level voltage regulation. Main Source from Semi：Datacenter Anatomy Part 1: Electrical Systems

Core takeaways

Keep voltage high for as long as practical. For a given power level, higher voltage means lower current, which reduces I²R losses and conductor size. Voltage is stepped down only as power gets closer to the load.

A data center is built around both capacity and continuity. The electrical system must deliver enough MW while also surviving equipment failure, maintenance and utility outages.

Main power chain layers. Utility / substation → MV distribution → transformers → LV switchgear → UPS / backup → PDU or busway → rack → PSU / power shelf → VRM → CPU / GPU.

Transformers change voltage; switchgear routes and protects power. Transformers step AC voltage up or down; switchgear isolates, distributes, protects and meters circuits.

UPS and generators solve different time horizons. UPS batteries respond almost instantly and bridge short interruptions; generators cover longer outages after they start and stabilise.

Redundancy is a design choice, not a single standard architecture. N, N+1, 2N, distributed redundancy designs trade off resilience, utilisation and capex.

Facility power vs IT power. Utility / facility capacity includes IT plus cooling and other loads（PUE）; Critical IT Power refers only to servers, storage and networking.

AC dominates traditional facility distribution, while chips ultimately run on DC. Conventional data centers distribute AC through much of the facility, then convert it to DC in server PSUs or rack power shelves before final chip-level regulation.

1. The power path: grid to rack

| Stage | Typical voltage / form | Main equipment | What it does |
| --- | --- | --- | --- |
| 1. Utility / transmission | HV or MV AC | Grid, transmission line, utility feed | Brings bulk power to the campus. |
| 2. Site substation | HV → MV AC | HV transformer, HV/MV switchgear | Steps transmission voltage down and distributes power across the campus. |
| 3. Building distribution | MV → LV AC | MV switchgear, MV/LV transformer | Brings voltage down to a level usable by facility electrical systems. |
| 4. Backup & transfer | Typically LV AC in traditional designs | Generator, ATS, UPS, batteries | Maintains power through grid outages and short interruptions. |
| 5. Data-hall distribution | LV AC | LV switchgear, PDU, RPP, busway, tap-off, power whips | Splits, protects, meters and routes power to rows and racks. |
| 6. Rack conversion | AC → DC | Rack PDU, PSU or central power shelf | Converts facility AC into DC suitable for IT hardware. |
| 7. Board / chip | DC → lower DC rails | DC/DC converters, VRMs | Steps voltage down to the very low voltages required by CPUs, GPUs and memory. |

Why power is stepped down gradually

Power loss in a conductor is approximately P_loss = I²R. For the same delivered power, raising voltage reduces current and therefore reduces resistive loss.

High and medium voltage are efficient for bulk transport, but require more insulation, clearance and safety controls. Lower voltage is therefore used closer to people and IT equipment.

In traditional architectures, a hyperscale campus may receive transmission-level power, step it to ~11–35 kV MV, and then step again to ~400–480 V class LV before the data hall. Exact values vary by country and operator.

Facility power vs. Critical IT power

| Metric | Meaning |
| --- | --- |
| Utility / Facility Power | Total electrical capacity available to the site, covering IT plus cooling, lighting and other facility loads. |
| Critical IT Power | Power capacity allocated to IT equipment only: servers, storage and networking. |

2. What each major component actually does

| Term | Plain-English function |
| --- | --- |
| Transformer | Changes AC voltage level through electromagnetic induction. It does not 'distribute' loads; its core job is voltage transformation. |
| Switchgear | A protected assembly containing breakers, switches, metering and relays. It routes, isolates and protects electrical circuits. |
| Circuit breaker | Interrupts abnormal current to protect equipment and prevent damage or fire. |
| ATS — Automatic Transfer Switch | Mechanically transfers a load between normal and backup sources, commonly utility and generator. |
| STS — Static Transfer Switch | Uses power electronics to transfer between two AC sources much faster than an ATS, typically downstream in critical distribution. |
| UPS — Uninterruptible Power Supply | Provides near-instant ride-through and power conditioning. Traditional double-conversion UPS uses rectifier + battery + inverter. |
| Generator | Provides longer-duration backup power after startup. In traditional hyperscale designs, large diesel or gas generators are common. |
| PDU — Power Distribution Unit | A broad term. Facility / floor PDUs distribute power downstream; rack PDUs distribute power within the rack. |
| RPP — Remote Power Panel | A smaller downstream panel that splits a larger feed into multiple protected branch circuits feeding racks. |
| Busway / busbar | A rigid high-current distribution conductor, often with tap-off points. Common in high-density data halls because it is modular and compact. |
| Power whip | A flexible cable assembly that carries power from a PDU / RPP / busway tap-off to the rack. |
| PSU — Power Supply Unit | Converts incoming AC to DC for server electronics in conventional server designs. |
| Power shelf | Centralises AC-to-DC conversion for an entire rack and feeds servers through a DC busbar; common in OCP-style architectures. |
| BBU — Battery Backup Unit | A distributed battery module close to the rack / load, providing short-duration backup without relying on a central UPS. |
| VRM — Voltage Regulator Module | Final-stage DC/DC conversion on or near the compute board, stepping the bus voltage down to chip-level rails. |

3. Redundancy: how data centers avoid a single point of failure

The basic language

| Architecture | Simple interpretation |
| --- | --- |
| N | Exactly the capacity required for normal operation; no spare capacity. |
| N+1 | Required capacity plus one additional component. If one unit fails or is maintained, the spare can cover it. |
| N+X | Required capacity plus X additional units. |
| 2N | Two complete, independent systems, each capable of supporting the full load. |
| 2N+1 | Two full systems plus an additional spare element. |
| Distributed redundant / catcher | Shared spare capacity is distributed across multiple blocks so utilisation is higher than a simple 2N design. |
| 3N/2 | Infrastructure sized to 1.5× the base load, providing redundancy with less duplication than 2N. |

How redundancy is implemented in practice

Traditional colocation designs often use independent A-side and B-side power paths. Dual-corded IT equipment can continue operating if one path is lost.

A Tier III / Rated 3 style design is commonly described as concurrently maintainable: planned maintenance can be performed without taking the IT service offline.

Tier IV / Rated 4 adds fault tolerance: a single unexpected infrastructure failure should not interrupt the critical load.

Hyperscalers may use architectures such as distributed redundancy, catcher systems or 4N3R rather than simple 2N, because these can improve asset utilisation and reduce capex per MW.

UPS vs. generator: the timing stack

| Layer | Response / duration | Role |
| --- | --- | --- |
| UPS / BBU | Milliseconds to minutes | Instant ride-through; keeps IT alive while another source starts or transfers. |
| Generator | Tens of seconds onward | Longer-duration backup after startup and stabilisation. |
| Grid / utility | Normal operating source | Primary energy supply in a conventional data center. |

4. AC vs. DC: the minimum you need to know

Why traditional data centers are mostly AC-distributed

The public grid is AC, and AC voltage can be stepped up or down efficiently with mature transformer technology.

Facility loads such as chillers, pumps, fans, lighting and many building systems are conventionally designed around AC.

Traditional server architectures therefore bring AC close to the rack and convert it to DC inside server PSUs or rack-level power shelves.

Why IT electronics ultimately need DC

Semiconductor devices do not operate directly from facility AC. CPUs, GPUs, memory and storage electronics require regulated DC rails.

The power chain therefore contains one or more AC/DC and DC/DC conversion stages before power reaches the silicon.

OCP-style racks centralise AC/DC conversion in a power shelf and distribute DC within the rack, instead of putting a separate rectifier inside every server.

Single-phase vs. three-phase AC

|  | Single-phase | Three-phase |
| --- | --- | --- |
| Typical use | Lower-power equipment and small loads | Data-center distribution and high-power equipment |
| Why it matters | Simple but lower power density | Higher power delivery for a given conductor / installation |

Typical voltage examples — directional, not universal

North America: 120/208 V is common for smaller loads; 480 V three-phase is common in higher-power facility distribution.

Europe: ~230 V single-phase and ~400 V three-phase are common.

Asia-Pacific: standards vary by country; ~220–230 V single-phase and ~380–400 V three-phase are common in many markets.

5. Essential terms

| Term | Meaning |
| --- | --- |
| HV / MV / LV | High / Medium / Low Voltage. Exact boundaries depend on standards and jurisdiction. |
| MVA vs. MW | MVA is apparent AC power; MW is real power. The ratio is governed by power factor. |
| Power factor | Ratio of real power to apparent power in an AC system. |
| Critical IT Power | Capacity reserved for servers, storage and networking. |
| Data hall | Room containing IT racks. |
| Pod | A modular block of IT capacity with a dedicated or semi-dedicated set of electrical / cooling infrastructure. |
| White space | Area occupied by IT racks and rack-adjacent equipment. |
| Grey space | Electrical / mechanical support area outside the main IT white space. |

A-side / B-side = two independent power paths for distribution redundancy; PUE = total facility energy ÷ IT equipment energy.