Data Center Cooling Systems

Notes based on SemiAnalysis（Cooling）, 2025

Cooling architecture is moving closer to the heat source as AI rack density rises. Traditional room-level air cooling remains highly relevant, but higher-density AI systems increasingly require rack-level or chip-level liquid cooling, supported by CDUs, facility water loops and heat-rejection equipment. Main Source from Semi：Datacenter Anatomy Part 2 – Cooling Systems

Core takeaways

Heat follows power. Almost all electrical power consumed by IT equipment becomes heat. Higher chip and rack power therefore translates directly into higher cooling requirements.

The real problem is heat density, not simply total MW. Air cooling can be very efficient at lower densities, but moving large amounts of heat from a small rack footprint requires rapidly increasing airflow, fan power and space.

Liquid cooling moves heat removal closer to the source. RDHx removes heat at the rack exhaust; Direct-to-Chip Liquid Cooling (DLC) removes heat directly from CPUs/GPUs through cold plates.

Liquid cooling does not eliminate facility cooling infrastructure. Heat still has to move from the chip or rack to a CDU / facility water loop and then to chillers, dry coolers, cooling towers or other heat-rejection systems.

Hybrid cooling is normal. A rack or data hall can combine DLC with air cooling or RDHx because not every component is necessarily liquid-cooled and legacy facilities may lack full liquid infrastructure.

CDU is the bridge between IT liquid loops and facility water. It typically contains a liquid-to-liquid heat exchanger, pumps and controls, managing temperature, flow and pressure while isolating the two loops.

Cooling efficiency is a system-level trade-off. PUE, WUE, inlet temperature, Delta T, fan energy, pump energy, chiller load and climate all matter. Optimising one metric can worsen another.

Free cooling and higher operating temperatures can materially reduce energy use. Hyperscalers achieved low PUE partly by using outside air / water conditions, higher inlet temperatures and highly optimised airflow.

Context note:  not a current market forecast or a definitive 2026 technology roadmap.

1. Cooling basics: how heat leaves a data center

| Stage | Heat-transfer medium | Typical equipment | Function |
| --- | --- | --- | --- |
| 1. Chip / server | Silicon → metal → air or liquid | TIM, heat sink, cold plate, server fans | Moves heat away from the chip package. |
| 2. Rack / data hall | Air and/or liquid | Fans, containment, RDHx, DLC loop | Collects heat from IT equipment. |
| 3. Facility loop | Water / coolant | CRAH, fan wall, CDU, pumps, heat exchangers | Transfers heat from the IT area to central cooling infrastructure. |
| 4. Refrigeration / economiser | Refrigerant and/or facility water | Chiller, waterside / airside economiser | Lowers coolant temperature when ambient conditions alone are insufficient. |
| 5. Heat rejection | Air and/or evaporating water | Dry cooler, air-cooled chiller, cooling tower | Rejects heat into the outside environment. |

Key physical concepts

1 kW of IT power produces approximately 1 kW of heat that must ultimately be removed.

Delta T is the temperature difference between inlet and outlet. A larger useful Delta T can reduce the airflow or liquid flow required to remove a given amount of heat.

Fan power is highly nonlinear: under the fan laws, power scales approximately with the cube of fan speed. Small reductions in airflow can therefore generate large energy savings.

SemiAnalysis cites ~165-170 CFM of airflow per kW of heat as a common rule of thumb for air-cooled servers.

PUE and WUE

| Metric | Definition | What to remember |
| --- | --- | --- |
| PUE | Total facility power / IT power | Lower is better, but comparisons can be distorted by where fan / pump power is counted. |
| WUE | Water use per unit of IT energy | Captures the water trade-off; evaporative systems can lower energy use but consume more water. |

2. Air-cooled architecture and indoor cooling units

| Technology | Where it sits | How it works | Typical positioning in the report |
| --- | --- | --- | --- |
| CRAC | Data hall | Local refrigeration cycle using refrigerant; paired with an outdoor condenser. | Simple but lower-capacity / lower-efficiency; more common in legacy or small facilities. |
| CRAH | Data hall | Fans blow return air across a coil supplied by central facility chilled water. | Better economics at scale but requires central piping, pumps and chillers / towers. |
| Fan Wall | Data hall / mechanical corridor | Large banks of fans and cooling coils move high volumes of air across an entire hall. | SemiAnalysis cites ~500-600 kW per unit; scalable for 5-10 MW data halls. |
| RDHx | Rack rear door | Water-cooled radiator captures heat from server exhaust air at the rack. | ~30-40 kW passive; >50 kW with active fans in the report. Often used as a bridge / hybrid solution. |

Why airflow management matters

Hot and cold air mixing wastes temperature headroom. Containment separates supply and return air and allows higher, more controlled inlet temperatures.

Modern greenfield facilities often use hot-aisle containment; cold-aisle containment also exists, but layout and maintenance trade-offs differ.

Hyperscalers use CFD (Computational Fluid Dynamics) to reduce recirculation, bypass airflow and unnecessary fan power.

RDHx: why it matters

RDHx can be thought of as an 'in-rack air handler': servers remain air-cooled, but rack exhaust heat is transferred into water immediately behind the rack. Proximity improves heat-exchanger effectiveness;

Trade-offs are higher rack-level capex, more moving parts and potentially higher fan power. In mixed deployments, a CDU may be added for liquid control.

RDHx and DLC can coexist in the same deployment;

3. Liquid cooling: the architecture to understand

Direct-to-Chip Liquid Cooling (DLC)

DLC places a cold plate directly on high-heat components such as CPUs and GPUs. Liquid carries heat away far more efficiently than moving the same heat through room air.

SemiAnalysis used the GB200 NVL72 (~120 kW rack) as the inflection point that brought DLC deployments into mainstream AI infrastructure discussion.

DLC does not necessarily cool every component. Memory, networking, power electronics or other components may still rely partly on air, so liquid-cooled racks can still require airflow.

The liquid path

| Layer | Typical components | Role | Key distinction |
| --- | --- | --- | --- |
| IT / rack loop | Cold plates, hoses, manifolds, quick disconnects | Collect heat directly from components. | Closest to sensitive electronics; cleanliness, leak management and pressure control are critical. |
| CDU | L2L heat exchanger, pumps, controls | Transfers heat between the IT loop and facility loop while controlling flow / temperature / pressure. | Creates hydraulic and fluid-quality separation between the two circuits. |
| Facility water loop | Pumps, piping, headers | Moves heat across the building to heat rejection. | May serve both liquid-cooled IT and other cooling equipment. |
| Heat rejection | Chiller, dry cooler, cooling tower, economiser | Rejects heat to the ambient environment. | DLC changes where heat is captured; it does not remove the need to reject that heat. |

CDU in plain English

A CDU is the interface between the data-center facility and liquid-cooled IT.

Core components are a liquid-to-liquid heat exchanger, pumps and control electronics.

It manages coolant flow rate, pressure drop and temperature, and can isolate IT coolant chemistry from facility water.

SemiAnalysis notes CDU capacities commonly above 1 MW, with many architecture variants.

What the 2025 report does - and does not - establish

It establishes the structural direction: rising AI density increases the value of moving cooling closer to the chip.

It does not establish that all future data centers become fully liquid-cooled, or that air cooling disappears.

The report's detailed discussion of L2L, L2A, immersion and two-phase cooling sits behind the paid section in the uploaded source; this note therefore does not invent conclusions that are not supported by the accessible material.

4. Chillers and heat rejection

| System | How heat is rejected | Strength | Trade-off |
| --- | --- | --- | --- |
| Water-cooled chiller + cooling tower | Refrigerant → condenser water → evaporative cooling tower | Very large unit capacity and high energy efficiency. | High water use; more piping, pumps and water treatment. |
| Air-cooled chiller | Refrigerant condenser rejects heat directly to outside air with fans | Simpler system and low water use. | Lower per-unit capacity and generally lower efficiency in hot conditions. |
| Dry cooler | Closed-loop water/glycol coil rejects heat to outdoor air | No evaporative water loss. | Performance depends strongly on ambient dry-bulb temperature; fan area can be large. |
| Adiabatic dry / air-cooled system | Evaporative pre-cooling lowers incoming air temperature before heat rejection | Hybrid compromise between water and energy use. | Still consumes some water and benefit falls in humid conditions. |
| Economiser / free cooling | Outside air or water conditions bypass / reduce compressor use | Can materially lower PUE and operating cost. | Highly dependent on climate and allowable IT inlet temperatures. |

Chiller basics

A chiller is essentially a large refrigeration machine. Its key components include an evaporator, compressor, condenser and expansion valve.

The compressor is the major energy-consuming component; reducing the required temperature lift lowers compressor work.

The report cites large water-cooled chillers at roughly 15-20 MW cooling capacity per unit, versus air-cooled units around ~2 MW at the high end of the example shown.

Chiller capacity is often quoted in refrigeration tons (RT): 1 RT ≈ 3.517 kW of cooling.

Energy vs. water trade-off

Evaporative cooling can reduce compressor energy by exploiting the wet-bulb temperature, especially in hot and dry climates.

The same mechanism consumes water. This is why a low-PUE design can still have high WUE.

Climate is therefore part of the cooling architecture: hot/humid locations are much harder for free cooling than cool or dry locations.

5. Hyperscaler design lessons from the report

| Operator / design | Cooling approach highlighted in the report | Industry lesson |
| --- | --- | --- |
| Microsoft | Airside free cooling / direct evaporative cooling in suitable climates; indirect evaporative variants elsewhere. | Avoiding chillers can lower capex and energy use, but water use can rise sharply in hot/dry locations. |
| Meta legacy 'H' | Free cooling, high server inlet temperature and low rack density. | Excellent PUE/WUE can come at the cost of lower density and slower buildout. |
| Google | Heavy use of waterside economisers and evaporative cooling towers; some chillerless sites. | Very low PUE can be achieved with higher water consumption - a clear energy/water trade-off. |
| AWS | Report infers substantial use of outside-air / free-cooling-style designs from site observations. | Hyperscalers standardise around internal workloads and can optimise more aggressively than multi-tenant colo operators. |

6. Essential terms

| Term | Meaning |
| --- | --- |
| DLC | Direct-to-Chip Liquid Cooling: cold plates remove heat directly from high-power components. |
| RDHx | Rear-Door Heat Exchanger: water-cooled radiator on the rack exhaust; servers themselves remain air-cooled. |
| CDU | Coolant Distribution Unit: interface between IT coolant and facility water. |
| L2L | Liquid-to-Liquid heat exchange; one liquid loop transfers heat to another without mixing fluids. |
| CRAC | Computer Room Air Conditioner; local refrigeration-based room cooling. |
| CRAH | Computer Room Air Handler; room air handler using central facility chilled water. |
| Fan Wall | Large, high-capacity bank of fans / coils serving a data hall. |
| Chiller | Mechanical refrigeration equipment that lowers water / coolant temperature. |
| Cooling Tower | Rejects heat from condenser water, commonly using evaporation. |
| Dry Cooler | Closed-loop heat rejection to outdoor air without evaporative water loss. |
| Economiser / Free Cooling | Uses ambient air or water conditions to reduce or bypass mechanical refrigeration. |
| Delta T | Temperature rise across a load or heat exchanger; a larger useful Delta T can reduce required flow. |
| PUE | Power Usage Effectiveness = total facility power / IT power. |
| WUE | Water Usage Effectiveness = water use per unit of IT energy. |