NVIDIA 800 VDC Architecture - Version 1

Whitepaper Reading Notes - Key Takeaways

Key Conepts

Rack power, not chip TDP alone, is the driver. GPU TDP typically rises incrementally, but larger NVLink domains can push rack power up by multiples. Hopper to GB300 is NVIDIA's example: +75% TDP, ~50x performance and ~3.4x rack power density.

800 VDC solves both scale and space constraints. Higher voltage reduces current for the same power, cutting conductor size, cable bulk and rack/facility power-distribution footprint. NVIDIA cites +157% power transfer through the same copper cross-section versus 415 VAC.

Energy storage becomes part of the power architecture, not an optional add-on. Synchronized GPU workloads can swing between ~30% and 100% rack power. Storage is used to smooth these swings before they propagate to the data center and grid.

Storage must be layered by timescale. Electrolytic capacitors are best suited to sub-100 ms events; mixed technologies cover ~100 ms to 10 s; batteries become more volume-efficient at longer durations.

The migration path is staged. Near term: side power racks for brownfield retrofits. Next: facility-level LV AC-to-800 VDC rectification. Longer term: MV rectifiers or solid-state transformers (SSTs) converting MV AC directly to 800 VDC.

800 VDC is the practical near-term choice; 1500 VDC is a longer-term option. 1500 VDC improves conductor utilization further, but indoor IT safety standards, certified components, creepage/clearance and arc-flash constraints are less mature.

Source: NVIDIA 800 VDC Architecture - official page / whitepaper access

1. Why the power architecture has to change

GPU generations increase chip power, but the bigger step-change comes from putting more GPUs into one tightly coupled NVLink domain. NVIDIA notes that rack power can rise 2x / 4x / 8x as the networking domain expands.

Copper is preferred for short-reach GPU interconnect because of performance and cost, so maximum compute performance increasingly depends on packing more GPUs into a limited physical radius - directly linking performance to power density.

Power infrastructure is therefore moving from a supporting function to a primary constraint on AI Factory design. A second design objective is to move power components out of the highest-value NVLink compute space.

2. Load swings make energy storage mandatory  |  The grid wants stable load; GPUs want highly dynamic power

LLM workloads alternate between intensive matrix computation and data exchange. Without buffering, rack demand can swing from ~30% idle to 100% utilization in short time interval.

NVIDIA describes four complementary mitigation methods: (1) reduce idle periods in software, (2) use energy storage, (3) burn power as a backstop, and (4) throttle GPU performance as a last resort.

Best practice is to absorb most swings with storage close to the GPU, minimizing data-center slew rates and RMS-current losses; burn power and throttling remain corner-case backstops.

Three relevant timescales: up to ~100 ms for GPU overshoot / idle events; ~1-5 s for checkpointing; minutes for full workload ramp-up / ramp-down. Storage technology should be selected accordingly.

3. Why 800 VDC  |  Higher voltage moves more power through less copper and with fewer conversion stages

| Voltage | Conductors | Power / cable area | vs. 415 VAC |
| --- | --- | --- | --- |
| 415 VAC | 4 | 0.6 kW/mm² | - |
| 480 VAC | 4 | 0.8 kW/mm² | +16% |
| 800 VDC | 3 | 1.7 kW/mm² | +157% |
| 1500 VDC | 3 | 3.1 kW/mm² | +382% |

Compared with 54 VDC in-rack distribution and 480 VAC facility distribution, 800 VDC reduces current, copper usage and cable bulk.

At the rack level, NVIDIA takes 800 VDC directly to the compute node, then converts 800 VDC to 12 VDC close to the GPU using a 64:1 LLC converter and matrix transformer.

Safety is built around touch-safe connectors, mechanical interlocks preventing disconnect under load, reinforced isolation and DC-specific protection - drawing on mature EV practices.

4. Facility architecture evolution  |  From retrofit to native DC

Today: MV step-down transformer -> LV switchboard -> AC UPS -> PDU / RPP or busway -> rack PSU -> 54 VDC.

Near-term retrofit: add an 800 VDC side power rack next to compute racks. This is not the end-state optimum because it adds conversion stages (Less efficient), but it enables higher rack density with minimal brownfield changes.

Longer term: MV rectifiers or SSTs convert medium-voltage AC (e.g., 35 kV) directly to 800 VDC, removing the conventional 480 VAC layer. NVIDIA views MV rectifiers as the more mature near-term path; multi-MW SSTs still face reliability and thermal/electrical-density challenges.

5. Grid interconnection and storage placement  |  AI Factories must become controllable electrical loads

Large synchronized GPU clusters can create rapid voltage and frequency deviations. Utilities therefore increasingly require load flexibility, controllability and predictability before approving interconnection.

Required capabilities include fast energy storage, GPU/workload pacing, coordinated compute + storage + facility controls, ramp-rate management, transient stability, harmonics/flicker control and voltage ride-through, etc.

Storage is deployed at both ends: facility/grid-side BESS for slower, larger-scale averaging and transfer support; short-duration capacitors near racks for fast power smoothing and slew-rate control.

Longer term, NVIDIA frames AI Factories as potential grid-supporting assets: they can absorb excess power, deliver supplemental power during stress, and support voltage/frequency stability through coordinated controls.

Personal Notes：Another bottleneck to keep in mind is that upgrades to existing data centers may require more transformers than expected, due to US bulk power grid equipment aging: 70% of transformers have been in service for more than 25 years. Spare capacity stands at only 20%, leaving no redundant buffer to absorb frequent and large load swings.

6. Voltage alternatives and industry implications  |  Why 800 VDC is the near-term convergence point

750 VDC: mature European industrial approach with a simplified two-wire system and compatibility with many 1000 V-class components.

+/-400 VDC: technically feasible and supported by OCP heritage, but midpoint grounding, protection and balancing become more complex at data-center scale.

1500 VDC: attractive for long-term conductor efficiency, but data-center indoor safety standards, certified components, clearance/creepage requirements and arc-flash controls are not yet as mature.

800 VDC therefore balances efficiency, equipment availability ( Adopted by EV industry ), protection simplicity and regulatory practicality, while preserving a pathway to higher voltages later.

7. What needs to mature in the ecosystem  |  The shift creates a new DC-native component stack

Standardization: common voltage windows, connector interfaces and current ratings.

DC-native equipment: rectifiers, distribution boards, breakers/protection, cabling, connectors, transfer-trip schemes and metering.

Safety and operations: grounding, fault isolation, arc-flash mitigation, maintenance procedures and technician training.