Inside the 800VDC Revolution - Part 1

Key Reading Notes

Based on SemiAnalysis, 26 May 2026

WHAT TO REMEMBER Semi Analysis sees 800V DC as a staged redesign of the entire AI data center power chain, not a single voltage change. The near-term opportunity is the HVDC sidecar; the structural change comes when 800V DC becomes facility-wide; the long-term prize is the SST. Across all phases, the more important question is where conversion, storage, protection and distribution functions move - and which suppliers capture those relocated value pools. Source: Inside the 800VDC Revolution – Part 1

Core takeaways

The transition is driven by rack density and system economics. At ~600 kW-class racks, 48-54 V distribution becomes impractical because current, copper mass, heat and power-hardware volume rise sharply. SemiAnalysis estimates ~5% facility-level power savings for the mature 800V DC architecture.

800V DC does not arrive all at once. Phases 1-2 retrofit existing AC facilities using an HVDC power rack / sidecar; Phase 3 moves rectification upstream and makes 800V DC the hall-level backbone; Phase 4 introduces MV SSTs.

Phase 1 adds equipment rather than removing it. The existing AC backbone largely remains, while a new HVDC power rack is added beside compute rack. Semi Analysis estimates: sidecar TAM peaking around $11bn in 2028.

Phase 2 is the first major structural inflection. 800V DC reaches the compute blade and the role of centralized LV UPS begins to decline. BBUs and supercapacitors move resilience and transient buffering closer to the load.

Phase 3 shifts the data hall from AC distribution to DC distribution. LV AC switchgear, floor PDUs and parts of the AC busway chain are removed or redesigned; MV rectifiers, battery racks and DC protection become more important.

Phase 4 is the SST end-state, but not yet mature. SSTs combine MV step-down and rectification into one programmable power-electronics platform. SemiAnalysis expects meaningful adoption only from 2029 and sizes 2030 SST TAM at $32bn.

Total electrical spend per MW changes less than the equipment mix. SemiAnalysis argues that value migrates across the chain: grey-space AC equipment loses share while white-space power electronics, storage and DC protection gain.

Execution constraints are material. Safety, grounding, DC fault interruption, cooling / auxiliary AC loads, standards and grid-interconnection rules can slow adoption even if the core physics are compelling.

1. Why 800V DC becomes necessary for compute racks

Low-voltage current becomes the bottleneck. At a fixed power level, higher voltage reduces current linearly. For 600 kW rack: 54 V structure requires : 11 kA; 800 V requires: 750 A, meaning significant deduction of copper usage.

Copper and thermal constraints scale non-linearly. Resistive losses scale with I²R. In practice, operators use the lower current to shrink conductors and busbars while still improving efficiency and reducing weight, heat and routing space.

Power hardware starts to crowd out compute. As rack power rises, low-voltage power shelves, busbars and cabling consume too much valuable rack volume. Moving to HVDC lets more of the rack remain dedicated to GPUs, networking and cooling.

Density improves compute economics. Larger scale-up domains depend on tightly packed compute. SemiAnalysis links denser racks to lower cost per token, making the electrical architecture an enabler of the compute architecture rather than a standalone facility choice.

2. Four-phase transition at a glance

| Phase | Timing | What changes | What remains | Key implication |
| --- | --- | --- | --- | --- |
| 1 | 2026/27 | HVDC power rack converts AC to 800V DC near the rack. | Most grey-space AC infrastructure; UPS remains. | Retrofit / future-proofing; additive electrical content. |
| 2 | 2027/28 | 800V DC becomes native to compute; DC/DC conversion moves onto / near the blade. | Power rack retrofit remains because facility DC is not ready. | UPS begins to lose its role; distributed storage grows. |
| 3 | Late 2028/29 | Central rectifier creates a facility-level 800V DC backbone. | MV grid interface and LV transformer remain in the base case. | LV AC distribution is replaced by DC distribution and protection. |
| 4 | >2029 | SST converts MV AC directly to 800V DC. | Auxiliary AC bus for cooling / building loads remains. | Transformer + rectifier collapse into one power-electronic platform. |

Adoption outlook

SemiAnalysis forecasts ~39 GW of incremental capacity powered by 800V DC by 2030.

Phases 1-2 are sidecar-heavy because the underlying facility remains AC-distributed.

The mix shifts around 2029 as facility-level HVDC and SST / MV-rectifier architectures become viable.

There is no single universal sidecar design: NVIDIA uses a monopolar 800V approach, while OCP Diablo 400 supports ±400V bipolar and 800V monopolar options.

3. Phase 1 - White-space retrofit

Architecture. MV AC → LV transformer → UPS → 415/480 V AC busway remains unchanged. The new element is a HVDC power rack (Sidecar) that converts AC to 800V DC and feeds adjacent IT racks.

Power rack functions. AC/DC rectification, short-duration BBU ride-through, optional capacitor / supercapacitor buffering, power management and DC output distribution.

Why the sidecar exists. It separates power conversion from the compute rack, improving serviceability and preserving rack volume for compute.

Economics. SemiAnalysis estimates ~$400-500k per power rack, around ~$0.5m/MW, with sidecar TAM peaking at ~$11bn in 2028.

Key nuance. Phase 1 is not yet forced by hardware: Vera Rubin racks can still be supported by conventional three-phase AC. Early adoption is therefore mainly future-proofing and efficiency-driven.

4. Phase 2 - 800V DC-native compute

Main change. 800V DC is routed deeper into the compute rack. Instead of a central rack-level power shelf converting 800V to ~50V, an on-blade / near-blade module performs the step-down closer to the load, which means HVDC power rack is required for the newer generation compute racks.

Why it matters. This is the point where 800V DC becomes driven by rack density rather than simply by operator preference.

UPS transition. Semi Analysis expects centralized LV UPS to progressively lose importance as BBU and supercapacitor storage become DC-coupled near the rack (can perform similar functionality of UPS with adoption of BESS). Google and Meta already use distributed backup approaches in parts of their fleets.

Not universal. Colocation providers and less vertically integrated operators may retain LV UPS longer for redundancy, operational simplicity and support for mixed AC workloads. MV UPS and facility-level BESS are alternative backup architectures.

5. Phase 3 - Facility-level 800V DC distribution

Rectification moves upstream. A central rectifier in grey space / outdoors converts 415V AC to 800V DC, and DC becomes the hall-level distribution backbone.

What disappears / shrinks. 480V AC switchgear below the rectifier, AC floor PDUs and much of the traditional AC distribution layer are removed or redesigned.

What replaces it. DC busway, DC distribution, battery racks, DC breakers / SSCBs, monitoring, etc.

Battery rack. Once AC/DC conversion moves upstream, the former power rack becomes primarily an energy-storage / distribution rack: DC/DC distribution units, BBU shelves and optional supercapacitors. SemiAnalysis estimates roughly ~$200k/MW of battery-rack content.

DC distribution and protection

Early deployments may favour feeder-only DC busway because live tap-offs are harder to implement safely at 800V DC.

DC has no natural zero-crossing, so fault arcs are harder to interrupt than in AC systems. This increases the importance of DC-rated breakers, isolation and solid-state circuit breakers (SSCBs).

SemiAnalysis sees several possible distribution products: rectifiers with integrated protected outputs, breaker-equipped DC tap-offs, and prefabricated grey-space pods combining rectifier + distribution + busway.

6. Phase 4 - SST end-state

Architecture. The SST replaces the LV transformer + LV AC/DC rectifier with a single MV-AC-to-800V-DC power-electronic system.

Why SSTs are attractive. Higher switching frequency enables a much smaller transformer core; SSTs also support active regulation, software control and potentially bidirectional power flow.

Technology stack. MV input stages rely on high-voltage SiC devices (3.3 kV-class and above); downstream 800V conversion can use lower-voltage SiC / GaN devices.

Current maturity. Public prototypes are around ~98-98.5% efficiency; the datacenter target is multi-MW units approaching 99%+ continuous efficiency with proven reliability.

Economics. SemiAnalysis estimates SST content at ~$1.0-1.5m/MW and 2030 SST TAM at ~$32bn, with significant competition from MV rectifiers.

Timing. Broad adoption is not expected before ~2029; certification, reliability and standards remain gating factors.

7. How the equipment value pool moves

| Category | Direction | SemiAnalysis logic |
| --- | --- | --- |
| Central LV UPS | Down | Ride-through and buffering migrate toward DC-coupled BBU / supercapacitor architectures; not all operators will eliminate UPS immediately. |
| Rack PDU / traditional rack AC power | Down | High-density racks increasingly receive HVDC rather than conventional AC at the rack interface. |
| LV AC switchgear / floor PDU | Down in Phase 3+ | Removed when 800V DC becomes the hall-level distribution backbone. |
| HVDC power rack / sidecar | Up, then down | Large Phase 1-2 opportunity, but temporary as rectification moves upstream. |
| DC busway & protection | Up | New DC distribution needs busway, breakers / SSCBs, isolation, sensing and monitoring. |
| BBU / supercapacitors | Up | Storage moves closer to compute to provide ride-through and absorb fast GPU transients. |
| SST / MV rectifier | Up materially | Phase 4 shifts conversion value upstream; SST becomes a new high-value category. |
| MV switchgear / grid interface | Largely resilient | Utility and most on-site generation remain AC; upstream MV infrastructure remains necessary. |
| Cooling / auxiliaries | Mostly AC | Chillers, pumps, fans, lighting and building systems still require an auxiliary AC bus, although DC-native components are emerging. |

8. Key implementation challenges

Safety and fault interruption. 800V DC requires new procedures for arc management, isolation, de-energisation and technician training.

Grounding architecture. ±400V bipolar and 800V monopolar systems create different protection-device, insulation-monitoring and fault-behaviour requirements; industry consensus is not yet established.

Cooling and auxiliary loads. The IT power chain can move to DC faster than the rest of the facility. Cooling, lighting, fire systems and building controls keep an AC auxiliary bus relevant.

Standards and certification. Busway standards are progressing, but many 800V DC categories still require site-specific engineering and AHJ / certification approval.

Grid interconnection. SST control, BESS state of charge and highly dynamic GPU loads change the facility’s grid-facing behaviour, increasing requirements for dynamic modelling, ride-through and utility coordination.